## Price Bid
Appendix - III
THE LAWRENCE SCHOOL , LOVEDALE
TENDER SCHEDULE / PRICE BID
Name of Work: Supply, Installation, Testing & Commissioning of 320 KVA DG set
S. No | Category | Description of work | Unit | Quantity | Rate | Amount
1 | DG | Supply, Installation, Testing & commissing of 320 KVA Disel Generator with aquastic as per CPCP norms along with adoptor box, control panel, etc., Make - Kirloskar Model - KG4-320WS1 | nos | 1
2 | Switch | Supply and fixing/replacing of 630 Amps MCCB in the Existing MV panel Make - Siemens | nos | 1
3 | Cable | Supply and Laying of 3.5 core 400 sq.mm x 2 run Aluminium armourd UG cable in burried cable trench of 4 feet depth and back filling with Brick and sand and termination. Make - Havels/Polycab | Meter | 40
4 | Termination | Supply and fixing of end termination for 3.5 core 400 sq.mm Aluminium armourd UG cable with suitable aluminium Lug, etc., Make - Comet | set | 4
5 | Earth pits | Supply and Providing of earth pit with 25mm dia 3 meter length copper bonded earthing rod with clamping connector, compound, 600x600 earth chamber, GI cover with copper earth plate 600x600x3 mm thick including accessories, painting, earth pit marking, etc., all as directed by the Engineer In-charge | nos | 4
6 | Earth bus | Supply, laying and connecting of 25x6mm x 2 runs of copper flat with necessary fixture | Meter | 60
7 | Exhaust system | Supply and providing Exhaust system with suitable steel support structure, all as per the norms of the Central Electrical Authority. | Lot | 1
8 | Preparation of drawing for approval & Inspection | Preparation and getting the drawing approval from Central Electrical Inspector, which is not restricted only for this project, overall additional load in the school campus to be considered | lot | 1
Inspection of Central Electrical Inspector and obtain saftey certificate, which is not restricted only for this project, overall additional load in the school campus to be considered
Incidental expenses for getting drawing approval and arranging Inspection, which is not restricted only for this project, overall additional load in the school campusto be considered
9 | MV panel board Extension | Supply, Installation, testing & commissing of 1200 x 450 x 2200 mm(LBH) MV panel extension with - 400 amps TPN double break switch - 4 nos (siemens make) including kwh meter & 80 x12mm Aluminium bus bar 2 run, Busbar chamber, cable chamber, etc., Note: Please refer the rough sketch in Appendix II | Lot | 1
10 | Fuel line | Supply, welding & installation of 1" MS fuel pipe line for generator day tank to Pumping location including flange and fittings etc. | Meter | 20
TOTAL (A)
GST @ 18%
TOTAL (B)
11 | Buy back | Less buy back of our existing Diesel Generator of 200 KVA (as is where is condition) | nos | 1
TOTAL ('C) - Buy Back
GST @ 18% for Buy back
TOTAL (D) - Buy Back
GRAND TOTAL (Total B (-) Total D)
Signature of the Contractor